## BoQ
Sl.No. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PART - A
A. | MV PANELS & DISTRIBUTION BOARDS
1.4 | UPS O/P CHANGE OVER PANEL i) 1 no. 40A, 2P MCB type COS ii) 2 sets of 2A, control MCB's | Set | 1
2 | MCB DISTRIBUTION BOARDS : ALL DOUBLE DOORS
Supply, installation, testing and commissioning of the following cubicle type 1.2 mm thick CRCA sheet steel enclosed powder coated with approved shade and partitions to segregate phase with approved covers, single / double door, factory made recessed in wall or surface mounted final distribution boards of the following description. All final DB's shall have outgoing with internal wiring brought upto terminal block for external cable connections.
NOTE : 1) Surface mounted DB's on walls shall be provided with suitable size frame work and neatly grouted on to wall and DB shall be fixed on to the frame work using bolts & nuts and other fixing accessories.
2) DB's conceald in wall shall include cut of necessary civil works and other fixing accessories.
3)The DB's shall be horizontal / vertical type as per configuration of incoming/outgoing feeders.
4)The DB's shall be factory made of approved make and necessary available higher size configured DB's shall be used.
2.1 | MDB
VTPN MCCB DB
Incomer:
1 No.100A, 4P MCCB ,
Outgoing:
4Nos. of 25/32. A SP MCBs (D curve)
| 4Nos. of 63 A TP MCBs (D curve) | Set | 1
2.3 | LDB - Type 2 FOR BRANCH
ETPN MCB DB
Incomer:
1 No.25A, 4P, ELCB + MCB (0-30mA) (B curve)
Outgoing:
| 16 Nos. of 6/10/16A, SP, MCBs (B curve) | Set | 1
2.4 | PDB
ETPN MCB DB
Incomer:
1 No. 40A. 4P. ELCB + MCB (0-100mA) (B curve)
Outgoing:
| 8 Nos. of 16/20/25/32 A, SP. MCBs (B curve) | Set | 1
2.6 | Computer DB - Type 1
SPN MCB DB
Incomer:
1 No. 40A, 2P, MCB (D curve)
Outgoing:
| 10 Nos. of 6/10 A SP MCBs (D curve) | Set | 1
4 | Supply, installation, testing and commissioning following sizes MCB in metallic enclosure. The MCB shall be wall mounted using necessary brackets and fixing accessories.
a) | 20/25/32A, DP MCB (D curve) | Set | 1
b) | 20/25/32A, 4P MCB (D curve) | Set | 1
PART - A TOTAL AMOUNT
PART - C
C. | WIRING SYSTEM
1 | Supply & Wiring for Lights, Ceiling fans, exhaust fan and 6A socket outlets using 3 x 1.5 sqmm flexible copper, 1100 volts grade PVC insulated FRLS wires drawn through 2mm thick, suitable size FR PVC conduit in concealed manner using necessary conduit accessories like junction boxes, Switch boxes, modular double plate and inner plate shall be of metal, bends, collars, clamps, ceiling roses, 6A/16A switches, Fan regulator and hook boxes, etc., and shall be flush mounted in brick wall or in the built up furnitures or on the surface of wall for surface installation as required. The rate for point wiring shall include the wiring from first point (light/switch) and then looping between lights/fans/6A socket outlets etc., Also the rate shall include earthing of each light, fan outlet boxes, switch control boxes, 6A sockets. (switches & sockets shall be of Anchor roma make /equivalent). The rate shall also include cost of civil works involved in fixing of boxes, replastering of walls chased. All the switch / sockets shall have stickers for identification
a) | Single light point controlled by a 6A SP switch. | Nos | 5
c) | Two light point controlled by a 6A SP switch | Nos | 5
d) | Two light point controlled by 2nos. 2Way 6A SP switch.
g) | Exhaust fan point (Single phase) controlled by a 6A SP switch and ceiling rose near the exhaust fan. /Wall Fan | Nos | 5
h) | Supply and wiring for call bell point with 3 x 1.5sqmm PVC insulated copper conductor FRLS wires in 20mm dia FR PVC conduit, including providing bell push with outlet box, inter-connectioin to the lighting circuit for power supply. | Nos | 2
2 | LIGHTING WIRING / SUB MAINS :
Supply & Drawing power wiring circuit /sub mains using flexible, copper conductor, FRLS wires of 1100V grade, PVC insulated wires drawn in 2mm thick suitable size FR PVC conduit. The rate shall also include running of PVC insulated copper conductor as earth wire. All circuits starting from the respected db should have ferrulling arrangements.
a) | 3 x 1.5 sqmm Copper wires in 20 mm dia PVC conduit | Rmtr. | 25
b) | 3 x 2.5 sqmm Copper wires in 20 mm dia PVC conduit | Rmtr. | 25
3 | POWER WIRING / SUB MAINS :
Supply & Drawing power wiring circuit /sub mains using flexible, copper conductor, FRLS wires of 1100V grade, PVC insulated wires drawn in 2mm thick suitable size FR PVC conduit. The rate shall also include running of PVC insulated copper conductor as earth wire. All circuits starting from the respected db should have ferrulling arrangements.
a) | 3 x 2.5 sqmm Copper wires in 20 mm dia PVC conduit. | Rmtr. | 50
b) | 3 x 4.0 sqmm Copper wires in 20 mm dia PVC conduit. | Rmtr. | 50
4 | POWER RECEPTACLES
DOMESTIC TYPE:
. | Supply & fixing of 3/5 pin, commerical combination type socket outlet with indicator mounted on a outlet box with necessary interconnection. The box shall be flush mounted in brick/stone wall. The switches shall be of type Anchor roma make / equivalent. The rate shall also include cost of civil works involved in fixing of boxes, replastering of walls chased. All the switch / sockets shall have stickers for identification
4.1 | RAW POWER SOCKET
a) | 6A socket outlet controlled by 6A SP Switch | Nos. | 5
b) | 2 Nos. 6A socket outlet controlled by 2 Nos. 6A SP Switch Soc.type2) | Nos.
c) | 6/16A socket outlet controlled by 1 Nos. 16A SP Switch | Nos.
d) | 16A Master switch with indicator | Nos.
e) | 16A, socket outlet | Nos.
f) | 16A, switch | Nos.
g) | 16A, switch with indicator | Nos.
4.2 | UPS/ RAW POWER SOCKET
a) | 6A socket outlet controlled by 6A SP Switch with indicator | Nos.
b) | 2 Nos. 6A socket outlet controlled by 2 Nos. 6A SP Switch Soc.type2) | Nos. | 15
c) | 3 Nos. 6A socket outlet controlled by 1 Nos. 16A SP Switch with indicator (Soc. Type-4) | Nos. | 20
d) | 6/16A socket outlet controlled by 1 Nos. 16A SP Switch with indicator (Soc. Type-3) | Nos. | 20
e) | 2 Nos. 6/16A socket outlet controlled by 2 Nos. 16A SP Switch with indicator (Soc. Type-5) | Nos. | 2
f) | 16A Master switch with indicator | Nos. | 2
g) | 16A, socket outlet | Nos.
h) | 16A, switch with indicator | Nos.
5 | INDUSTRIAL SOCKETS :
5.1 | Supply, installation, testing and commissioning following sizes MCB in IP 65 Weather proof enclosure. The rate shall include cost of MCB isolator. The MCB shall be wall mounted using necessary brackets and fixing accessories.
a) | 63A, 4P MCB isolator (D curve) | Set
a) | 32A, 4P MCB isolator (D curve) | Set | 2
PART - C TOTAL AMOUNT
PART - D
D. | SUPPLY AND INSTALLATION OF LIGHT & FAN FIXTURES
1 | Supply, installation, testing and commissioning of following type light and fan fixtures with all necessary fixing accessories as required. The efficacy of the LED lamp shall be not less than 100lm/Watt
1.1 | 1 x 20W, 4000K, 4 Feet LED tube, Surface/suspension light fixture of type REGALBATTENT 8UPTO1X22WSSBSWH + CRYSTAL 1213T8DSTL20WLED865SGLASS of similar to Havells make/equivalent. | Nos. | 6
1.2 | 2 x 20W, 4000K, 4 Feet LED tube, Surface/suspension light fixture of type REGALBATTENT 8UPTO2X22WSSBSWH + CRYSTAL 1213T8DSTL20WLED865SGLASS of similar to Havells make/equivalent. | Nos. | 2
1.3 | 15W-18W LED Recessed down Lighter of type ENDURANEODLR18WLED830S of similar to Havells make/equivalent. | Nos. | 10
1.4 | 15W LED surface down Lighter of type INTEGRANEOSURFA CEDLS15WLED857S of similar to Havells make/equivalent. | Nos. | 5
1.5 | 5W LED Recessed down Lighter of type ORBITDLR5WLED830S of similar to Havells make/equivalent. | Nos. | 0
1.6 | 42W, 4000K LED, square surface mounted Light fixture (2' x 2') of type PLUTOSURFA PLUTOSURFA CE2X2PLS42WLED857S of similar to havells make/equivalent. | Nos.
1.7 | 36W, 4000K LED, square Recess mounted Light fixture (2' x 2') of type BZRSQL 36W GZi WH of similar to bajaj make/equivalent. | Nos. | 10
1.8 | Supply and Installation of LED STRIP indoor, 10W / meter including driver and necessary fixing accessories as required | Mts | 0
1.9 | Supply and fixing of 1200mm sweep, ceiling fan without fan regulator and shall be of crompton /equivalent. | Nos. | 0
1.1 | Supply and fixing of 400mm sweep, WALL fan of crompton /equivalent. | Nos. | 0
1.11 | Supply and fixing of 150/225mm dia. single phase. exhaust fan with necessary angle iron bracket. | Nos. | 0
1.12 | Supply & fixing of Timer for UPS room Exhaust Fans | Nos. | 0
2 | INSTALLATION OF LIGHT & FAN FIXTURES (existing)
2.1 | Installation of 15/5W LED surface / recess down lighter | Nos | 30
2.2 | 2' x 2', surface / recess, mounted Light fixture | Nos | 10
2.3 | 1200/900.mm sweep, ceiling fan without fan regulator and shall be of crompton /equivalent. | Nos | 0
2.4 | 150/225mm dia. single phase. exhaust fan/Wall Fan with necessary angle iron bracket. | Nos | 0
PART - D TOTAL AMOUNT
PART - E
F. | TELEPHONE SYSTEM
1 | Supply and laying of 2mm thick FR PVC conduit with all necessary accessories like junction boxes, pull boxes. G.I fish wires and other fixing accessories as required. The rate shall also include chasing of walls, floor and plastering of the chased portion etc; all complete as required.
a) | 20mm dia | M | 100
2 | Supply and wiring for telephone outlet with 0.51mm dia, copper conductor, PVC insulated, unarmoured, telephone cable in existing conduit.
2.1 | 2 pair | M | 100
3 | Supply and wiring of multicore 0.51mm, copper conductor, PVC Insulated, PVC sheathed, armoured telephone cable laid drawn through existing trench/cable tray / wall supports with all necessary accessories as required.
a) | 5 Pair Cable | M | 0
b) | 10 Pair Cable | M | 30
c) | 20 Pair Cable | M | 35
d) | 50 Pair Cable | M | 0
4 | Supply and installation of clip on plug type telephone outlet with interconnection of the outlet. The cover plate of telephone shall match with the other wiring accessories. (Telephone socket outlet shall be of modular of type Anchor roma / equivalent) . | Nos. | 20
5 | Supply, installation, testing & commissioning of telephone junction box. The junction box shall be with sheet steel enclosure enclosing krone connector and shall be provided with padlock arrangement.
b) | 10 Pair TJB. | Nos. | 1
c) | 20 Pair TJB. | Nos. | 1
PART - F TOTAL AMOUNT
PART - G
G. | DATA SYSTEM
1 | Supply and laying of 2mm thick FR PVC conduit with all necessary accessories like junction boxes, pull boxes. G.I fish wires and other fixing accessories as required. The rate shall also include chasing of walls, floor and plastering of the chased portion etc all complete as required.
a) | 25 mm dia | M | 200
2 | Supply, installation of Dual RJ-45, CAT -6 information outlet with necessary back mount box and other fixing accessories. (socket outlet shall be of modular of type Dilink / equivalent) . | Nos. | 15
3 | Supply, drawing and connecting of cat-6, UTP cable in existing conduit for LAN network. | M | 600
4 | Supply and connecting of UTP cat -6 mounting cords
a) | 4' 0" long | Nos. | 15
b) | 7' 0'" long | Nos. | 15
5 | Supply, installation , testing & commissioning of patch panel with CAT-6 I/O mounted on existing rack with all necessary fixing accessories. The rate shall include cost of ferrule, numbering, stickering & necessary fixing accessories as required
a) | 24 port jack panel | Nos. | 2
6 | Supply, installation , testing & commissioning of 600mm width, 500mm depth wall mounted, closed rack with 1 PDU 1 tray1 cable manager and all necessary fixing accessories as required.
a) | 9 U rack | Nos. | 0
b) | 12 U rack | Nos. | 0
c) | 15 U rack | Nos. | 0
PART - G TOTAL AMOUNT
PART - H
H. | TV SYSTEM
1 | Supply and installation of T.V. Co-axial socket outlet with inter connection of the outlet The cover plate of T.V. Co-axial socket outlet shall match with other wiring accessories. ( The socket outlet shall be of make Anchor roma /equivalent) The rate shall also include cost of civil works involved in fixing of boxes. | Nos | 1
2 | Supply & drawing of RG 6 co-axial cable in existing conduit. | M | 15
3 | Supply and laying of 2mm thick FR PVC conduit with all necessary accessories like junction boxes, pull boxes. G.I fish wires and other fixing accessories as required. The rate shall also include chasing of walls, floor and plastering of the chased portion etc all complete as required.
a) | 25 mm dia | M | 15
PART - H TOTAL AMOUNT
PART -I
I. | PA SYSTEM
1 | Supply and wiring as per colour code transparent speaker cable 2.50sqmm PVC insulated stranded copper wire 2 runs through ISI grade 20mm conduit for speakers. | M | 100
2 | Supply and providing 9W recessed type speakers on ceiling CS 663 T Ahuja make speaker. | Nos | 2
PART - I TOTAL AMOUNT
PART - J
J. | MISCELLANEOUS WORKS:
1 | Dismantling of existing wiring, conduit, light fixtures, ceiling fan, exhaust fan, light plug, switch boards, DB's. LT cables, determination cables, complete dismantling of electrical components in the building and making good of the damages to surfaces, Bundling all the wires, cables, and securing of all other dismantled materials and storing it, at the location allotted / identified by the project manager within in the premises, all complete as required. | LS | 1
TOTAL PART-J:-
ABSTRACT
PART - A | MV PANELS & DISTRIBUTION BOARDS |  |  | 0
PART - B | LT CABLES AND CABLE END TERMINATION :
PART - C | WIRING SYSTEM |  |  | 0
PART - D | SUPPLY AND INSTALLATION OF LIGHT & FAN FIXTURES |  |  | 0
PART - F | TELEPHONE SYSTEM |  |  | 0
PART - G | DATA SYSTEM |  |  | 0
PART - H | TV SYSTEM |  |  | 0
PART -I | PA SYSTEM |  |  | 0
PART - J | MISCELLANEOUS WORKS: |  |  | 0
| TOTAL |  |  | 0